## QA_simple
질문분류 | comment | idx | 폴더 선택 (검색 범위 지정) | lang | query | gt_answer | path_1 | filename_1 | page_1 | content_1 | path_2 | filename_2 | page_2 | content_2 | path_3 | filename_3 | page_3 | content_3 | path_4 | filename_4 | page_4 | content_4 | path_5 | filename_5 | page_5 | content_5 | path_6 | filename_6 | page_6 | content_6 | path_7 | filename_7 | page_7 | content_7 | path_8 | filename_8 | page_8 | content_8 | path_9 | filename_9 | page_9 | content_9 | path_10 | filename_10 | page_10 | content_10 | path_11 | filename_11 | page_11 | content_11 | path_12 | filename_12 | page_12 | content_12 | path_13 | filename_13 | page_13 | content_13
simple | spring, 유압방식(hydrolic), spring 방식을 써야한다, 유압방식을 쓰면 안된다, circuit breaker 부분 참고 | 1 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the operating method of the circuit breaker, such as spring-operated or hydraulic-operated? | The operating method of the circuit breaker shall be electromechanical (motor-spring). If they are of another type (for example: hydro-mechanical), they must be expressly approved by RE in particular. In any case, the accumulation of energy will have to be mechanical (using springs). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 8 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.10. DRIVE MECHANISMS
simple | local control cubicle 관련 부분은 모두 확인, standalone, integral, | 2 | 3. Customer Standard Specifications/Spain/REE | eng | Shall the local control cubicle (LCC) be a standalone type or integral type | The local control cabinets shall be located independently of the switchgears. If this is not possible, they will be mounted on the switchgears as long as it is easy to access for staff. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS
simple | 중국제 제품을 사용하면 안된다는 제약이 있음. 특정 국가에서 제작된 부품을 반드시 사용해야 한다 같은 제약이 있음. 자국기업 제품 사용을 권하는 문구들이 있음, Chinese, China | 3 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any restrictions on using Chinese or foreign products? | The local control cabinet of the switchgear, supplied by the manufacturer, will preferably be manufactured and tested in Spain. Only with specific prior approval from RE would the manufacturing and testing of this cabinet be permitted outside of Spain. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS | [43 empty] | https://login.microsoftonline.com/1cb54445-8763-4a0c-aedb-bf7c72027e4e/oauth2/authorize?client%5Fid=00000003%2D0000%2D0ff1%2Dce00%2D000000000000&response%5Fmode=form%5Fpost&response%5Ftype=code%20id%5Ftoken&resource=00000003%2D0000%2D0ff1%2Dce00%2D000000000000&scope=openid&nonce=83027551F626E658A3DAE9C199AB5BE7E03A6D313C0C61AD%2D44D70A2609C2E5D4B4AACE0CBB322F23FF1E2431B23BD7B256E2722C7EE3CBAC&redirect%5Furi=https%3A%2F%2Fhdhyundaigroup%2Esharepoint%2Ecom%2F%5Fforms%2Fdefault%2Easpx&state=OD0w&claims=%7B%22id%5Ftoken%22%3A%7B%22xms%5Fcc%22%3A%7B%22values%22%3A%5B%22CP1%22%5D%7D%7D%7D&wsucxt=1&cobrandid=11bd8083%2D87e0%2D41b5%2Dbb78%2D0bc43c8a8e8a&client%2Drequest%2Did=04938ca1%2Db0a8%2D4000%2De126%2D27436ec5fb44&sso_reload=true
simple | 중국제 제품을 사용하면 안된다는 제약이 있음. 특정 국가에서 제작된 부품을 반드시 사용해야 한다 같은 제약이 있음. 자국기업 제품 사용을 권하는 문구들이 있음, Chinese, China | 4 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any restrictions or preferences regarding the manufacturing or testing location of the gas-insulated switchgear, its components, or related systems such as the local control cabinet, mentioned in the specification? | The local control cabinet of the switchgear, supplied by the manufacturer, will preferably be manufactured and tested in Spain. Only with specific prior approval from RE would the manufacturing and testing of this cabinet be permitted outside of Spain. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS
simple | controlled switching device, point-on-wave controller, phase synchronizing, 오타나는 경우도 있어서 control, point, wave | 5 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the point-on-wave controller? | The use of controlled switching relays aims to reduce the dielectric stress that may appear on certain occasions in the switching switches themselves, in the surrounding substation equipment and in the network as a whole. In principle, the applications for which RE considers the use of controlled maneuver relays are: • Application 1. Reduction of insertion currents and surges in the energization of capacitor banks, insulated cables and long transmission lines. • Application 2. Reduction of inrush currents and voltage distortion in energization of reactances and power transformers. Application 3. Elimination of RE ignitions in the de-energization of power reactors. The proper application of controlled maneuver relays requires that the switch satisfy certain minimum requirements in terms of: • Precision and repeatability in opening and closing times under temperature variations, coil tension variation, spring energy variation or long period of time between consecutive maneuvers. • Sufficiently high dielectric capacity of the contact system (RDDS and RRDS). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 59 | Shielded switchgear 220 kV, double busbar, SF6 insulation SWITCHES WITH SYNCHRONIZED MANEUVERING RELAYS
simple |  | 6 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the Controlled Switching Device, Point-On-Wave Controller, and Phase Synchronizing Device? | The use of controlled switching relays aims to reduce the dielectric stress that may appear on certain occasions in the switching switches themselves, in the surrounding substation equipment and in the network as a whole. In principle, the applications for which RE considers the use of controlled maneuver relays are: • Application 1. Reduction of insertion currents and surges in the energization of capacitor banks, insulated cables and long transmission lines. • Application 2. Reduction of inrush currents and voltage distortion in energization of reactances and power transformers. Application 3. Elimination of RE ignitions in the de-energization of power reactors. The proper application of controlled maneuver relays requires that the switch satisfy certain minimum requirements in terms of: • Precision and repeatability in opening and closing times under temperature variations, coil tension variation, spring energy variation or long period of time between consecutive maneuvers. • Sufficiently high dielectric capacity of the contact system (RDDS and RRDS). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 59 | Shielded switchgear 220 kV, double busbar, SF6 insulation SWITCHES WITH SYNCHRONIZED MANEUVERING RELAYS
simple |  | 7 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements for the gas leakage rate of the gas insulated switchgear? | The relative leakage rate of each compartment shall not exceed 0.1% per year for the whole of life of the GIS. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 7 | 5.1.1 General
simple |  | 8 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements for the insulation medium of the 132 kV gas-insulated switchgear? | It is indicated in the table in Section 5.4, Technical Performance Summary, that the interrupting medium and insulation medium for 132 kV GIS shall be SF₆ gas. However, it is also mentioned that Endeavour Energy’s preference is for the use of switchgear that does not contain SF6 gas given its management and global warming potential (GWP) where alternative cost-effective technologies are available. Cost-efficient offers of equipment containing SF6 will be considered however weighting will be applied in the evaluation process to preference equipment with no or minimal SF6. SF6 management, environmental impact and disposal costs will be considered in the evaluation process. A similar evaluation weighting will be applied to all gas insulated switchgear, regardless of gas used (except dry-air) weighted by its GWP. Pressurised dry air, or any gas other than SF6, insulated switchboards utilising vacuum circuit breakers will be considered, and are preferred, where this technology has been adequately proven. The supplier of the SF6 switchgear shall have a return policy whereby they will accept responsibility for disposal of the SF6 switchgear and any remaining SF6 gas or by-products. The supplier shall also accept SF6 gas that is evacuated during maintenance for the whole life of the switchgear. SF6 management, environmental and disposal costs will be considered in the evaluation process. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 8 | 5.3.1 Insulating gas management and global warming potential (GWP) | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary
simple |  | 9 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any specific requirements or preferences mentioned in the document regarding the insulation medium for the 132 kV gas-insulated switchgear, such as the use of SF6 gas or its alternatives? | It is indicated in the table in Section 5.4, Technical Performance Summary, that the interrupting medium and insulation medium for 132 kV GIS shall be SF₆ gas. However, it is also mentioned that Endeavour Energy’s preference is for the use of switchgear that does not contain SF6 gas given its management and global warming potential (GWP) where alternative cost-effective technologies are available. Cost-efficient offers of equipment containing SF6 will be considered however weighting will be applied in the evaluation process to preference equipment with no or minimal SF6. SF6 management, environmental impact and disposal costs will be considered in the evaluation process. A similar evaluation weighting will be applied to all gas insulated switchgear, regardless of gas used (except dry-air) weighted by its GWP. Pressurised dry air, or any gas other than SF6, insulated switchboards utilising vacuum circuit breakers will be considered, and are preferred, where this technology has been adequately proven. The supplier of the SF6 switchgear shall have a return policy whereby they will accept responsibility for disposal of the SF6 switchgear and any remaining SF6 gas or by-products. The supplier shall also accept SF6 gas that is evacuated during maintenance for the whole life of the switchgear. SF6 management, environmental and disposal costs will be considered in the evaluation process. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 8 | 5.3.1 Insulating gas management and global warming potential (GWP) | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary
simple |  | 10 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | What is the rated continuous current of the 132 kV GIS? | It is indicated in the table in Section 5.4, Technical Performance Summary, Part C1 - ETS 0012 am0 - 66 kV and 132 kV Pressurized GIS, that the rated minimum feeder current shall be 2000 A, while the busbar current shall be 2500 A. However, it is stated in the table in Section 17.1, Table 5.4: Technical Performance Summary, Part C General Specification - 132 kV GIS - Jan 2022 Final, that the rated minimum current is 2500 A for both the feeder and the busbar. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C General Specification - 132kV GIS - Jan 2022 Final.pdf | 38 | 17. AMENDMENTS TO ETS 0012 17.1 Table 5.4: Technical Performance Summary
simple |  | 11 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the operating method of the circuit breaker, such as spring-operated or hydraulic-operated? | The closing mechanism for the circuit breaker of the 132 kV GIS shall be a motor-charged spring. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 10 | 5.4 Technical performance summary | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 14 | 5.5.4.1 Circuit breaker operating mechanism and enclosure | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 15 | 5.5.4.1 Circuit breaker operating mechanism and enclosure
simple |  | 12 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the on-line PD monitoring system? | "No, there is no requirement for an on-line PD monitoring system. However, there are other requirements related to monitoring systems: internal arc detection, a voltage detection system, and a gas pressure monitoring system. Please refer to Section 5.6.2.1 for internal arc detection, Section 5.6.2.2 for the voltage detection system, and Section 5.6.2.3 for the gas pressure monitoring system." | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 30 | 5.6.2.1 Internal arc detection, 5.6.2.2 Voltage detection system | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 31 | 5.6.2.3 Gas pressure monitoring system
simple |  | 13 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the monitoring systems? | No, there is no requirement for an on-line PD monitoring system. However, there are other requirements related to monitoring systems: internal arc detection, a voltage detection system, and a gas pressure monitoring system. Please refer to Section 5.6.2.1 for internal arc detection, Section 5.6.2.2 for the voltage detection system, and Section 5.6.2.3 for the gas pressure monitoring system. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 30 | 5.6.2.1 Internal arc detection, 5.6.2.2 Voltage detection system | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 31 | 5.6.2.3 Gas pressure monitoring system
simple |  | 14 | 1. International Standards/IEC | eng | In accordance with IEC 62271-203_Edition 2.0_2011-08, what type of type tests are required for gas insulated switchgear? | The mandatory type tests are as follows: a) Tests to verify the insulation level of the equipment and dielectric tests on auxiliary circuits b) Tests to prove the radio interference voltage (RIV) level (if applicable) c) Tests to prove the temperature rise of any part of the equipment and measurement of the resistance of the main circuit d) Tests to prove the rated peak and the rated short time withstand current e) Tests to verify the making and breaking capacity of included switching devices. f) Tests to prove the satisfactory operation of the included switching devices g) Tests to prove the strength of enclosures h) Verification of the degree of protection of the enclosure i) Gas tightness tests j) Electromagnetic compatibility tests (EMC) k) Additional tests on auxiliary and control circuits l) Tests on partitions m) Tests to prove the satisfactory operation at limit temperatures n) Tests to prove performance under thermal cycling and gas tightness tests on insulators o) Corrosion test on earthing connections (if applicable) p) X-radiation test procedure for vacuum interrupters (if applicable) The type tests, when requested by the user, are as follows: q) Tests to assess the effects of arcing due to an internal fault r) Corrosion test on enclosures (if applicable) | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 28 | Table 5
simple |  | 15 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | eng | What is the rated SF6 gas pressure at 20°C of the gas insulated model of 145SP-3? | The rated SF6 gas pressure at 20°C of 145SP-3 is 0.60 MPa for the circuit breaker and 0.50 MPa for others. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 5 | Rated Circuit-breaker : 0.60 MPa Others : 0.50 MPa
reasoning |  | 16 | 2. Type Test Reports/300SR/245 kV 63 kA MS (2024) & 1. International Standards/IEC | eng | Please organize the type test report numbers for the 245 kV 63 kA GIS model 300SR, aligned with the type test required by IEC 62271-203_Edition 2.0_2011-08. | 첨부 파일 (245 kV 63 kA GIS_Type test report summary) 참조 | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 30 | Table 5 | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024
simple |  | 17 | 1. International Standards | kor | IEC와 IEEE 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 어떻게 되나요? | 1. IEC 62271-203 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 아래와 같습니다. GIS의 각 개별 구획에서 대기로의 누출 및 다른 구획 간 누출의 상대 누기율은 기기의 예상 운영 기간 동안 연간 0.5 %를 초과하지 않아야 합니다. 단, 형식 시험에서의 최대 상대 누기율은 연간 0.1 %를 초과하지 않아야 합니다. 2. IEEE C37.122 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 아래와 같습니다. 어느 한 개별 가스 구획에서 대기로의 SF₆ 가스 누기율은 형식 시험 결과 연간 0.1 %를 초과하지 않아야 하며, 정기 시험 결과 연간 0.5 %를 초과하지 않아야 합니다. | International_Standards__IEC | IEC 62271-203_Edition 3.0_2022-05.pdf | 22 | 6.16.3 Closed pressure systems for gas | International_Standards__IEEE | IEEE Std C37.122-2010.pdf | 31 | 6.16 Gas and vacuum tightness
reasoning |  | 18 | 2. Type Test Reports/300SR/245 kV 63 kA MS (2024) & 1. International Standards/IEC | kor | 245 kV 63 kA GIS 모델 300SR에 대한 성적서 번호를 IEC 62271-203_Edition 2.0_2011-08에서 요구하는 형식시험 항목에 맞게 정리해 주세요. | 첨부 파일 (245 kV 63 kA GIS_Type test report summary) 참조. 첨부 파일에 나와 있는 표가 답안으로 나와야 함. | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 30 | Table 5 | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024
simple |  | 19 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델의 온도상승 시험은 어떤 규격에 따라 진행된 것이고 주위 온도 몇 도를 기준으로 진행된 건가요? | 온도 상승 시험은 IEC 62271-203 Edition 2.0 (2011) 규격에 따라 진행되었으며, 주위 온도 24.5 °C 조건에서 수행되었습니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 3 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 17 | 2 Temperature-rise test
reasoning |  | 20 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) & 1. International Standards/IEC | kor | 실제 설치 장소의 주위 온도가 55 °C 일 경우 145SP-3 모델이 허용 온도 한계를 충족하는 건가요? | 145SP-3 모델의 온도 상승 시험은 IEC 62271-203 Edition 2.0 (2011) 규격에 따라 진행되었으며, 주위 온도 24.5 °C 조건에서 수행되었습니다. 그러나 실제 설치 장소의 주위 온도가 55 °C이므로, 각 항목의 온도 상승 제한치를 15 K 낮춰야 합니다. 이 기준을 적용하여 재해석한 결과, CB 접점(Contact of CB), CB 연결부(Connection of CB), CB 외함(CB enclosure) 등이 기준을 충족하지 못합니다. 따라서, 145SP-3 모델은 주위 온도가 55 °C인 조건에서 IEC 62271-203 Edition 2.0 (2011)의 온도 상승 시험 요구 사항을 만족하지 못합니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 14 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 15 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 16 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 17 | 2 Temperature-rise test
reasoning |  | 21 | 1. International Standards/IEC | kor | IEC에 따른 145 kV GIS의 Capacitive current switching 시험의 Duty 1과 Duty 2 전류 시험값은 어떻게 되나요? | IEC 62271-100 Edition 3.0 (2021) 규격에 따르면, capacitive current switching 시험의 요구 사항은 다음과 같습니다. - test-duty 1 (LC1, CC1, BC1) : 10 to 40 % of the rated capacitive breaking current - test-duty 2 (LC2, CC2, BC2) : not less than 100 % of the rated capacitive breaking current 1. 145 kV GIS의 Rated line-charging breaking current : 50 A - line-charging current, test-duty 1 LC1의 test current : 5 ~ 20 A - line-charging current, test-duty 2 LC2의 test current : ≥ 50 A 2. 145 kV GIS의 Rated cable-charging breaking current : 160 A - line-charging current, test-duty 1 CC1의 test current : 16 ~ 64 A - line-charging current, test-duty 2 CC2의 test current : ≥ 160 A 3. 145 kV GIS의 Rated capacitor bank breaking current : 400 A - capacitor bank current, test-duty 1 BC1의 test current : 40 ~ 160 A - capacitor bank current, test-duty 2 BC2의 test current : ≥ 400 A | International_Standards__IEC | IEC 62271-100_Edition 3.0_2021-07.pdf | 56 | Table 1 Table 33 7.111.9.1 | International_Standards__IEC | IEC 62271-100_Edition 3.0_2021-07.pdf | 183 | Table 1 Table 33 7.111.9.1 | International_Standards__IEC | IEC 62271-101_Edition 3.0_2021-07.pdf | 184 | Table 1 Table 33 7.111.9.1
simple |  | 22 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델의 Capacitive current switching 시험에서 실제 시험 전류값은 어떻게 되나요? | 145SP-3 모델은 다음과 같은 시험값으로 Capacitive current switching 시험이 수행되었습니다. - Line-charging current & line-charging current, test-duty 1: LC1, CC1의 시험 전류: 18.2 A - Line-charging current & line-charging current, test-duty 2: LC2, CC2의 시험 전류: 162 A Capacitor bank breaking current 시험은 수행되지 않은 것으로 확인됩니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 10 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 11 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 12 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 13 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 14 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 15 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 16 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 17 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 18 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 20 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 21 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 22 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 23 | Breaking current, phase value Breaking current, phase value
reasoning |  | 23 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델을 115 kV, 30 MVAR capacitor bank에 연결할 경우, 전류값은 얼마이며 성적서상으로 차단 성능을 보증할 수 있는지 검토해 주세요. | 115 kV, 30 MVAR capacitor bank에 흐르는 전류는 최대 150 A입니다. KEMA 2517-15 V4(LC-CC, 50-60 Hz, 1.3-1.5) 성적서에 따르면, 145 kV 차단기는 LC2 및 CC2 조건에서 162 A의 전류를 차단하는 것으로 확인되었습니다. 따라서, 최대 150 A의 전류가 흐르는 115 kV, 30 MVAR capacitor bank에 연결된 경우, 해당 차단기는 문제없이 전류를 차단할 수 있다고 판단됩니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 10 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 11 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 12 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 13 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 14 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 15 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 16 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 17 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 18 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 20 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 21 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 22 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 23 | Breaking current, phase value Breaking current, phase value
simple |  | 24 | 3. Customer Standard Specifications | kor | Electrical endurance E2 class를 요구하는 수용가를 알려주세요. | 오만 OETC에서는 33 kV 차단기에 대해 Electrical Endurance E2 Class를 요구하고 있습니다. | Customer_Standard_Specifications__Oman__OETC | 1. Standard Specification for Substation OETC-AMD-O-AMT-M-040.pdf | 2095 | 2.5 Electrical Endurance Class
simple |  | 25 | 3. Customer Standard Specifications/Saudi Arabia/SEC | kor | Duplex는 어떠한 경우에 적용해야 하는지 알려주세요. | 해안선으로부터 반경 25 km 이내의 WOA 및 SOA 지역에서는 도장과 용융 아연 도금을 결합한 **듀플렉스 시스템(Duplex System)을 적용해야 합니다. | Customer_Standard_Specifications__Saudi_Arabia__SEC | 01-TMSS-01-R3.pdf | 16 | Table-12
reasoning |  | 26 | 1. International Standards/IEC | kor | GIS의 정격 전류가 3150 A이고 온도 상승 시험의 주위 온도가 40°C, 최소 허용 온도가 80°C일 때, 부하 전류가 2500 A인 경우 허용 가능한 주위 온도는 몇 도인가요? | IEC 62271-306 Edition 1.0 (2012) 규격의 식 5에 따라 허용되는 주위 온도는 53.6 °C입니다. | International_Standards__IEC | IEC 62271-306_Edition 1.0_2012-12.pdf | 46 | 5.2.2.2 Continuous load current capability based on actual ambient temperature

## QA_reasoning
질문분류 | comment | idx | 폴더 선택 (검색 범위 지정) | lang | query | gt_answer | path_1 | filename_1 | page_1 | content_1 | path_2 | filename_2 | page_2 | content_2 | path_3 | filename_3 | page_3 | content_3 | path_4 | filename_4 | page_4 | content_4 | path_5 | filename_5 | page_5 | content_5 | path_6 | filename_6 | page_6 | content_6 | path_7 | filename_7 | page_7 | content_7 | path_8 | filename_8 | page_8 | content_8 | path_9 | filename_9 | page_9 | content_9 | path_10 | filename_10 | page_10 | content_10 | path_11 | filename_11 | page_11 | content_11 | path_12 | filename_12 | page_12 | content_12 | path_13 | filename_13 | page_13 | content_13
simple |  | 1 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the operating method of the circuit breaker, such as spring-operated or hydraulic-operated? | The operating method of the circuit breaker shall be electromechanical (motor-spring). If they are of another type (for example: hydro-mechanical), they must be expressly approved by RE in particular. In any case, the accumulation of energy will have to be mechanical (using springs). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 8 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.10. DRIVE MECHANISMS
simple |  | 2 | 3. Customer Standard Specifications/Spain/REE | eng | Shall the local control cubicle (LCC) be a standalone type or integral type | The local control cabinets shall be located independently of the switchgears. If this is not possible, they will be mounted on the switchgears as long as it is easy to access for staff. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS
simple |  | 3 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any restrictions on using Chinese or foreign products? | The local control cabinet of the switchgear, supplied by the manufacturer, will preferably be manufactured and tested in Spain. Only with specific prior approval from RE would the manufacturing and testing of this cabinet be permitted outside of Spain. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS | [43 empty] | https://login.microsoftonline.com/1cb54445-8763-4a0c-aedb-bf7c72027e4e/oauth2/authorize?client%5Fid=00000003%2D0000%2D0ff1%2Dce00%2D000000000000&response%5Fmode=form%5Fpost&response%5Ftype=code%20id%5Ftoken&resource=00000003%2D0000%2D0ff1%2Dce00%2D000000000000&scope=openid&nonce=83027551F626E658A3DAE9C199AB5BE7E03A6D313C0C61AD%2D44D70A2609C2E5D4B4AACE0CBB322F23FF1E2431B23BD7B256E2722C7EE3CBAC&redirect%5Furi=https%3A%2F%2Fhdhyundaigroup%2Esharepoint%2Ecom%2F%5Fforms%2Fdefault%2Easpx&state=OD0w&claims=%7B%22id%5Ftoken%22%3A%7B%22xms%5Fcc%22%3A%7B%22values%22%3A%5B%22CP1%22%5D%7D%7D%7D&wsucxt=1&cobrandid=11bd8083%2D87e0%2D41b5%2Dbb78%2D0bc43c8a8e8a&client%2Drequest%2Did=04938ca1%2Db0a8%2D4000%2De126%2D27436ec5fb44&sso_reload=true
simple |  | 4 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any restrictions or preferences regarding the manufacturing or testing location of the gas-insulated switchgear, its components, or related systems such as the local control cabinet, mentioned in the specification? | The local control cabinet of the switchgear, supplied by the manufacturer, will preferably be manufactured and tested in Spain. Only with specific prior approval from RE would the manufacturing and testing of this cabinet be permitted outside of Spain. | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 9 | Shielded switchgear 220 kV, double busbar, SF6 insulation 4.12. CONTROL CABINETS
simple |  | 5 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the point-on-wave controller? | The use of controlled switching relays aims to reduce the dielectric stress that may appear on certain occasions in the switching switches themselves, in the surrounding substation equipment and in the network as a whole. In principle, the applications for which RE considers the use of controlled maneuver relays are: • Application 1. Reduction of insertion currents and surges in the energization of capacitor banks, insulated cables and long transmission lines. • Application 2. Reduction of inrush currents and voltage distortion in energization of reactances and power transformers. Application 3. Elimination of RE ignitions in the de-energization of power reactors. The proper application of controlled maneuver relays requires that the switch satisfy certain minimum requirements in terms of: • Precision and repeatability in opening and closing times under temperature variations, coil tension variation, spring energy variation or long period of time between consecutive maneuvers. • Sufficiently high dielectric capacity of the contact system (RDDS and RRDS). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 59 | Shielded switchgear 220 kV, double busbar, SF6 insulation SWITCHES WITH SYNCHRONIZED MANEUVERING RELAYS
simple |  | 6 | 3. Customer Standard Specifications/Spain/REE | eng | Are there any requirements regarding the Controlled Switching Device, Point-On-Wave Controller, and Phase Synchronizing Device? | The use of controlled switching relays aims to reduce the dielectric stress that may appear on certain occasions in the switching switches themselves, in the surrounding substation equipment and in the network as a whole. In principle, the applications for which RE considers the use of controlled maneuver relays are: • Application 1. Reduction of insertion currents and surges in the energization of capacitor banks, insulated cables and long transmission lines. • Application 2. Reduction of inrush currents and voltage distortion in energization of reactances and power transformers. Application 3. Elimination of RE ignitions in the de-energization of power reactors. The proper application of controlled maneuver relays requires that the switch satisfy certain minimum requirements in terms of: • Precision and repeatability in opening and closing times under temperature variations, coil tension variation, spring energy variation or long period of time between consecutive maneuvers. • Sufficiently high dielectric capacity of the contact system (RDDS and RRDS). | Customer_Standard_Specifications__Spain__REE | ET082_ed8_Eng_NO_OFFICIAL.pdf | 59 | Shielded switchgear 220 kV, double busbar, SF6 insulation SWITCHES WITH SYNCHRONIZED MANEUVERING RELAYS
simple |  | 7 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements for the gas leakage rate of the gas insulated switchgear? | The relative leakage rate of each compartment shall not exceed 0.1% per year for the whole of life of the GIS. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 7 | 5.1.1 General
simple |  | 8 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements for the insulation medium of the 132 kV gas-insulated switchgear? | It is indicated in the table in Section 5.4, Technical Performance Summary, that the interrupting medium and insulation medium for 132 kV GIS shall be SF₆ gas. However, it is also mentioned that Endeavour Energy’s preference is for the use of switchgear that does not contain SF6 gas given its management and global warming potential (GWP) where alternative cost-effective technologies are available. Cost-efficient offers of equipment containing SF6 will be considered however weighting will be applied in the evaluation process to preference equipment with no or minimal SF6. SF6 management, environmental impact and disposal costs will be considered in the evaluation process. A similar evaluation weighting will be applied to all gas insulated switchgear, regardless of gas used (except dry-air) weighted by its GWP. Pressurised dry air, or any gas other than SF6, insulated switchboards utilising vacuum circuit breakers will be considered, and are preferred, where this technology has been adequately proven. The supplier of the SF6 switchgear shall have a return policy whereby they will accept responsibility for disposal of the SF6 switchgear and any remaining SF6 gas or by-products. The supplier shall also accept SF6 gas that is evacuated during maintenance for the whole life of the switchgear. SF6 management, environmental and disposal costs will be considered in the evaluation process. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 8 | 5.3.1 Insulating gas management and global warming potential (GWP) | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary
simple |  | 9 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any specific requirements or preferences mentioned in the document regarding the insulation medium for the 132 kV gas-insulated switchgear, such as the use of SF6 gas or its alternatives? | It is indicated in the table in Section 5.4, Technical Performance Summary, that the interrupting medium and insulation medium for 132 kV GIS shall be SF₆ gas. However, it is also mentioned that Endeavour Energy’s preference is for the use of switchgear that does not contain SF6 gas given its management and global warming potential (GWP) where alternative cost-effective technologies are available. Cost-efficient offers of equipment containing SF6 will be considered however weighting will be applied in the evaluation process to preference equipment with no or minimal SF6. SF6 management, environmental impact and disposal costs will be considered in the evaluation process. A similar evaluation weighting will be applied to all gas insulated switchgear, regardless of gas used (except dry-air) weighted by its GWP. Pressurised dry air, or any gas other than SF6, insulated switchboards utilising vacuum circuit breakers will be considered, and are preferred, where this technology has been adequately proven. The supplier of the SF6 switchgear shall have a return policy whereby they will accept responsibility for disposal of the SF6 switchgear and any remaining SF6 gas or by-products. The supplier shall also accept SF6 gas that is evacuated during maintenance for the whole life of the switchgear. SF6 management, environmental and disposal costs will be considered in the evaluation process. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 8 | 5.3.1 Insulating gas management and global warming potential (GWP) | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary
simple |  | 10 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | What is the rated continuous current of the 132 kV GIS? | It is indicated in the table in Section 5.4, Technical Performance Summary, Part C1 - ETS 0012 am0 - 66 kV and 132 kV Pressurized GIS, that the rated minimum feeder current shall be 2000 A, while the busbar current shall be 2500 A. However, it is stated in the table in Section 17.1, Table 5.4: Technical Performance Summary, Part C General Specification - 132 kV GIS - Jan 2022 Final, that the rated minimum current is 2500 A for both the feeder and the busbar. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 9 | 5.4 Technical performance summary | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C General Specification - 132kV GIS - Jan 2022 Final.pdf | 38 | 17. AMENDMENTS TO ETS 0012 17.1 Table 5.4: Technical Performance Summary
simple |  | 11 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the operating method of the circuit breaker, such as spring-operated or hydraulic-operated? | The closing mechanism for the circuit breaker of the 132 kV GIS shall be a motor-charged spring. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 10 | 5.4 Technical performance summary | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 14 | 5.5.4.1 Circuit breaker operating mechanism and enclosure | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 15 | 5.5.4.1 Circuit breaker operating mechanism and enclosure
simple |  | 12 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the on-line PD monitoring system? | "No, there is no requirement for an on-line PD monitoring system. However, there are other requirements related to monitoring systems: internal arc detection, a voltage detection system, and a gas pressure monitoring system. Please refer to Section 5.6.2.1 for internal arc detection, Section 5.6.2.2 for the voltage detection system, and Section 5.6.2.3 for the gas pressure monitoring system." | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 30 | 5.6.2.1 Internal arc detection, 5.6.2.2 Voltage detection system | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 31 | 5.6.2.3 Gas pressure monitoring system
simple |  | 13 | 3. Customer Standard Specifications/Australia/Endeavour Energy | eng | Are there any requirements regarding the monitoring systems? | No, there is no requirement for an on-line PD monitoring system. However, there are other requirements related to monitoring systems: internal arc detection, a voltage detection system, and a gas pressure monitoring system. Please refer to Section 5.6.2.1 for internal arc detection, Section 5.6.2.2 for the voltage detection system, and Section 5.6.2.3 for the gas pressure monitoring system. | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 30 | 5.6.2.1 Internal arc detection, 5.6.2.2 Voltage detection system | Customer_Standard_Specifications__Australia__Endeavour_Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf | 31 | 5.6.2.3 Gas pressure monitoring system
|  | 14 | 1. International Standards/IEC | eng | In accordance with IEC 62271-203_Edition 2.0_2011-08, what type of type tests are required for gas insulated switchgear? | The mandatory type tests are as follows: a) Tests to verify the insulation level of the equipment and dielectric tests on auxiliary circuits b) Tests to prove the radio interference voltage (RIV) level (if applicable) c) Tests to prove the temperature rise of any part of the equipment and measurement of the resistance of the main circuit d) Tests to prove the rated peak and the rated short time withstand current e) Tests to verify the making and breaking capacity of included switching devices. f) Tests to prove the satisfactory operation of the included switching devices g) Tests to prove the strength of enclosures h) Verification of the degree of protection of the enclosure i) Gas tightness tests j) Electromagnetic compatibility tests (EMC) k) Additional tests on auxiliary and control circuits l) Tests on partitions m) Tests to prove the satisfactory operation at limit temperatures n) Tests to prove performance under thermal cycling and gas tightness tests on insulators o) Corrosion test on earthing connections (if applicable) p) X-radiation test procedure for vacuum interrupters (if applicable) The type tests, when requested by the user, are as follows: q) Tests to assess the effects of arcing due to an internal fault r) Corrosion test on enclosures (if applicable) | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 28 | Table 5
simple |  | 15 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | eng | What is the rated SF6 gas pressure at 20°C of the gas insulated model of 145SP-3? | The rated SF6 gas pressure at 20°C of 145SP-3 is 0.60 MPa for the circuit breaker and 0.50 MPa for others. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 5 | Rated Circuit-breaker : 0.60 MPa Others : 0.50 MPa
reasoning |  | 16 | 2. Type Test Reports/300SR/245 kV 63 kA MS (2024) & 1. International Standards/IEC | eng | Please organize the type test report numbers for the 245 kV 63 kA GIS model 300SR, aligned with the type test required by IEC 62271-203_Edition 2.0_2011-08. | 첨부 파일 (245 kV 63 kA GIS_Type test report summary) 참조 | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 30 | Table 5 | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024
|  | 17 | 1. International Standards | kor | IEC와 IEEE 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 어떻게 되나요? | 1. IEC 62271-203 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 아래와 같습니다. GIS의 각 개별 구획에서 대기로의 누출 및 다른 구획 간 누출의 상대 누기율은 기기의 예상 운영 기간 동안 연간 0.5 %를 초과하지 않아야 합니다. 단, 형식 시험에서의 최대 상대 누기율은 연간 0.1 %를 초과하지 않아야 합니다. 2. IEEE C37.122 규격에 따른 고압 차단기의 SF₆ 가스 연간 허용 누기율 기준은 아래와 같습니다. 어느 한 개별 가스 구획에서 대기로의 SF₆ 가스 누기율은 형식 시험 결과 연간 0.1 %를 초과하지 않아야 하며, 정기 시험 결과 연간 0.5 %를 초과하지 않아야 합니다. | International_Standards__IEC | IEC 62271-203_Edition 3.0_2022-05.pdf | 22 | 6.16.3 Closed pressure systems for gas | International_Standards__IEEE | IEEE Std C37.122-2010.pdf | 31 | 6.16 Gas and vacuum tightness
reasoning |  | 18 | 2. Type Test Reports/300SR/245 kV 63 kA MS (2024) & 1. International Standards/IEC | kor | 245 kV 63 kA GIS 모델 300SR에 대한 성적서 번호를 IEC 62271-203_Edition 2.0_2011-08에서 요구하는 형식시험 항목에 맞게 정리해 주세요. | 첨부 파일 (245 kV 63 kA GIS_Type test report summary) 참조. 첨부 파일에 나와 있는 표가 답안으로 나와야 함. | International_Standards__IEC | IEC 62271-203_Edition 2.0_2011-08.pdf | 30 | Table 5 | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024
simple |  | 19 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델의 온도상승 시험은 어떤 규격에 따라 진행된 것이고 주위 온도 몇 도를 기준으로 진행된 건가요? | 온도 상승 시험은 IEC 62271-203 Edition 2.0 (2011) 규격에 따라 진행되었으며, 주위 온도 24.5 °C 조건에서 수행되었습니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 3 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 17 | 2 Temperature-rise test
reasoning |  | 20 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) & 1. International Standards/IEC | kor | 실제 설치 장소의 주위 온도가 55 °C 일 경우 145SP-3 모델이 허용 온도 한계를 충족하는 건가요? | 145SP-3 모델의 온도 상승 시험은 IEC 62271-203 Edition 2.0 (2011) 규격에 따라 진행되었으며, 주위 온도 24.5 °C 조건에서 수행되었습니다. 그러나 실제 설치 장소의 주위 온도가 55 °C이므로, 각 항목의 온도 상승 제한치를 15 K 낮춰야 합니다. 이 기준을 적용하여 재해석한 결과, CB 접점(Contact of CB), CB 연결부(Connection of CB), CB 외함(CB enclosure) 등이 기준을 충족하지 못합니다. 따라서, 145SP-3 모델은 주위 온도가 55 °C인 조건에서 IEC 62271-203 Edition 2.0 (2011)의 온도 상승 시험 요구 사항을 만족하지 못합니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 14 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 15 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 16 | 2 Temperature-rise test | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KERI 2016TC00736.pdf | 17 | 2 Temperature-rise test
reasoning |  | 21 | 1. International Standards/IEC | kor | IEC에 따른 145 kV GIS의 Capacitive current switching 시험의 Duty 1과 Duty 2 전류 시험값은 어떻게 되나요? | IEC 62271-100 Edition 3.0 (2021) 규격에 따르면, capacitive current switching 시험의 요구 사항은 다음과 같습니다. - test-duty 1 (LC1, CC1, BC1) : 10 to 40 % of the rated capacitive breaking current - test-duty 2 (LC2, CC2, BC2) : not less than 100 % of the rated capacitive breaking current 1. 145 kV GIS의 Rated line-charging breaking current : 50 A - line-charging current, test-duty 1 LC1의 test current : 5 ~ 20 A - line-charging current, test-duty 2 LC2의 test current : ≥ 50 A 2. 145 kV GIS의 Rated cable-charging breaking current : 160 A - line-charging current, test-duty 1 CC1의 test current : 16 ~ 64 A - line-charging current, test-duty 2 CC2의 test current : ≥ 160 A 3. 145 kV GIS의 Rated capacitor bank breaking current : 400 A - capacitor bank current, test-duty 1 BC1의 test current : 40 ~ 160 A - capacitor bank current, test-duty 2 BC2의 test current : ≥ 400 A | International_Standards__IEC | IEC 62271-100_Edition 3.0_2021-07.pdf | 56 | Table 1 Table 33 7.111.9.1 | International_Standards__IEC | IEC 62271-100_Edition 3.0_2021-07.pdf | 183 | Table 1 Table 33 7.111.9.1 | International_Standards__IEC | IEC 62271-101_Edition 3.0_2021-07.pdf | 184 | Table 1 Table 33 7.111.9.1
simple |  | 22 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델의 Capacitive current switching 시험에서 실제 시험 전류값은 어떻게 되나요? | 145SP-3 모델은 다음과 같은 시험값으로 Capacitive current switching 시험이 수행되었습니다. - Line-charging current & line-charging current, test-duty 1: LC1, CC1의 시험 전류: 18.2 A - Line-charging current & line-charging current, test-duty 2: LC2, CC2의 시험 전류: 162 A Capacitor bank breaking current 시험은 수행되지 않은 것으로 확인됩니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 10 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 11 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 12 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 13 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 14 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 15 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 16 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 17 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 18 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 20 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 21 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 22 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 23 | Breaking current, phase value Breaking current, phase value
reasoning |  | 23 | 2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | kor | 145SP-3 모델을 115 kV, 30 MVAR capacitor bank에 연결할 경우, 전류값은 얼마이며 성적서상으로 차단 성능을 보증할 수 있는지 검토해 주세요. | 115 kV, 30 MVAR capacitor bank에 흐르는 전류는 최대 150 A입니다. KEMA 2517-15 V4(LC-CC, 50-60 Hz, 1.3-1.5) 성적서에 따르면, 145 kV 차단기는 LC2 및 CC2 조건에서 162 A의 전류를 차단하는 것으로 확인되었습니다. 따라서, 최대 150 A의 전류가 흐르는 115 kV, 30 MVAR capacitor bank에 연결된 경우, 해당 차단기는 문제없이 전류를 차단할 수 있다고 판단됩니다. | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 10 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 11 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 12 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 13 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 14 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 15 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 16 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 17 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 18 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 20 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 21 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 22 | Breaking current, phase value Breaking current, phase value | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | 23 | Breaking current, phase value Breaking current, phase value
simple |  | 24 | 3. Customer Standard Specifications | kor | Electrical endurance E2 class를 요구하는 수용가를 알려주세요. | 오만 OETC에서는 33 kV 차단기에 대해 Electrical Endurance E2 Class를 요구하고 있습니다. | Customer_Standard_Specifications__Oman__OETC | 1. Standard Specification for Substation OETC-AMD-O-AMT-M-040.pdf | 2095 | 2.5 Electrical Endurance Class
simple |  | 25 | 3. Customer Standard Specifications/Saudi Arabia/SEC | kor | Duplex는 어떠한 경우에 적용해야 하는지 알려주세요. | 해안선으로부터 반경 25 km 이내의 WOA 및 SOA 지역에서는 도장과 용융 아연 도금을 결합한 **듀플렉스 시스템(Duplex System)을 적용해야 합니다. | Customer_Standard_Specifications__Saudi_Arabia__SEC | 01-TMSS-01-R3.pdf | 16 | Table-12
reasoning |  | 26 | 1. International Standards/IEC | kor | GIS의 정격 전류가 3150 A이고 온도 상승 시험의 주위 온도가 40°C, 최소 허용 온도가 80°C일 때, 부하 전류가 2500 A인 경우 허용 가능한 주위 온도는 몇 도인가요? | IEC 62271-306 Edition 1.0 (2012) 규격의 식 5에 따라 허용되는 주위 온도는 53.6 °C입니다. | International_Standards__IEC | IEC 62271-306_Edition 1.0_2012-12.pdf | 46 | 5.2.2.2 Continuous load current capability based on actual ambient temperature

## 데이터 list
filter | filename | 데이터 개수 | path | International_Standards__IEC | International_Standards__IEEE | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | Type_Test_Reports__300SR__245_kV_50_kA_MS_2020 | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024 | Customer_Standard_Specifications__Australia__Endeavour_Energy
1. International Standards/IEC | IEC 60099-4_Edition 3.0_2014-06.pdf | 99 | International_Standards__IEC | IEC 60099-4_Edition 3.0_2014-06.pdf | IEEE Std C37.010-2016.pdf | KEMA 2515-15 V3(50-60Hz, 1.5).pdf | CESI B9017250 TTR (60Hz).PDF | KEMA 3055-22 R0_Temperature rise.pdf | 111Sketch 1 - Typical 132kV GIS FDR process interface.pdf
1. International Standards/IEC | IEC 60137_Edition 7.0_2017-06.pdf |  | International_Standards__IEEE | IEC 60137_Edition 7.0_2017-06.pdf | IEEE Std C37.04-2018.pdf | KEMA 2516-15 V3(50-60Hz, 1.3).pdf | CESI B9017251_TTR (50Hz).pdf | KEMA 3078-22 R0_Mechanical_IP_Pressure.pdf | Part C General Specification - 132kV GIS - Jan 2022 Final.pdf
1. International Standards/IEC | IEC 60376_Edition 3.0_2018-05.pdf |  | Type_Test_Reports__145SP3__145_kV_40_kA_MS_2017 | IEC 60376_Edition 3.0_2018-05.pdf | IEEE Std C37.04-2018_errata.pdf | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf | CESI C0000059-1 TTC (60Hz).PDF | KERI 20TC100154_Insulator_Partition.PDF | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf
1. International Standards/IEC | IEC 60480_Edition 2.0_2004-10.pdf |  | Type_Test_Reports__300SR__245_kV_50_kA_MS_2020 | IEC 60480_Edition 2.0_2004-10.pdf | IEEE Std C37.09-2018.pdf | KEMA 2523-15 V3(60Hz, 1.5).pdf | CESI C0000060-1_TTC (50Hz).PDF | KERI 22TB100134_Dielectric_RIV.PDF | Part C2 - ETS0014 - Control panel fabrication and installation.pdf
1. International Standards/IEC | IEC 61869-1_Edition 2.0_2023-06.pdf |  | Type_Test_Reports__300SR__245_kV_63_kA_MS_2024 | IEC 61869-1_Edition 2.0_2023-06.pdf | IEEE Std C37.09-2018_errata.pdf | KEMA 2524-15 V3(60Hz, 1.3).pdf | KERI 19TB101031_LCCC.PDF | KERI 22TB100169_STC.PDF | Part C3 - SDI 526 - Design of Substation Secondary Systems.pdf
1. International Standards/IEC | IEC 61869-2_Edition 1.0_2012-09.pdf |  | Customer_Standard_Specifications__Australia__Endeavour_Energy | IEC 61869-2_Edition 1.0_2012-09.pdf | IEEE Std C37.122-2010.pdf | KERI 2016TC00558.pdf | KERI 20TB100010_ES Induced current switching.pdf | KERI 22TB100175_Internal.PDF | Part C4 - SDI 545 - Acceptable purity limits for SF6 gas.pdf
1. International Standards/IEC | IEC 61869-3_Edition 1.0_2011-07.pdf |  | Customer_Standard_Specifications__Oman__OETC | IEC 61869-3_Edition 1.0_2011-07.pdf |  | KERI 2016TC00736.pdf | KERI 20TB100021_내아크.pdf | KERI 22TB100176_ES Making.PDF | Part C5 - SDI547 - Alarm and tripping requirements in SF6 and dry air equipment.pdf
1. International Standards/IEC | IEC 62271-100_Edition 2.1_2012-09.pdf |  | Customer_Standard_Specifications__Saudi_Arabia__SEC | IEC 62271-100_Edition 2.1_2012-09.pdf |  | KERI 2016TC00925.pdf | KERI 20TB100025_OP2.PDF | KERI 23STL00038_Certificate.PDF | Part C6 - SDI535 - Site testing and pre-commissioning.pdf
1. International Standards/IEC | IEC 62271-100_Edition 2.2_2017-06.pdf |  | Customer_Standard_Specifications__Spain__Iberdrola | IEC 62271-100_Edition 2.2_2017-06.pdf |  | KERI 2017TC00055.pdf | KERI 20TB100027_Bus-transfer current switching tests.PDF | KERI 24TB100176_Out of phase switching.PDF
1. International Standards/IEC | IEC 62271-100_Edition 3.0_2021-07.pdf |  | Customer_Standard_Specifications__Spain__REE | IEC 62271-100_Edition 3.0_2021-07.pdf |  | KERI 2017TC00070.pdf | KERI 20TB100028-R1_ES Making.pdf | KERI 24TB100187_Capacitive switching.pdf | Customer_Standard_Specifications__Oman__OETC
1. International Standards/IEC | IEC 62271-101_Edition 2.0_2012-10.pdf |  |  | IEC 62271-101_Edition 2.0_2012-10.pdf |  | KERI 2017TC00445.pdf | KERI 20TB100029_STC.PDF |  | 1. Standard Specification for Substation OETC-AMD-O-AMT-M-040.pdf
1. International Standards/IEC | IEC 62271-101_Edition 3.0_2021-07.pdf |  |  | IEC 62271-101_Edition 3.0_2021-07.pdf |  |  | KERI 20TC100045_온도상승시험.PDF
1. International Standards/IEC | IEC 62271-101_Edition 3.0_2021-10 (Corrigendum 1).pdf |  |  | IEC 62271-101_Edition 3.0_2021-10 (Corrigendum 1).pdf |  |  | KERI 20TC100065_LI AC PD RIV 보조회로 0기압.pdf |  | Customer_Standard_Specifications__Saudi_Arabia__SEC
1. International Standards/IEC | IEC 62271-102_Edition 1.1_2012-02.pdf |  |  | IEC 62271-102_Edition 1.1_2012-02.pdf |  |  | KERI 20TC100101_외함압력시험.PDF |  | 01-TMSS-01-R3.pdf
1. International Standards/IEC | IEC 62271-102_Edition 2.0_2018-05.pdf |  |  | IEC 62271-102_Edition 2.0_2018-05.pdf |  |  | KERI 20TC100102_IP TEST.PDF |  | 32-TMSS-02-R2-A1.pdf
1. International Standards/IEC | IEC 62271-102_Edition 2.1_2022-09 (Amendment 1).pdf |  |  | IEC 62271-102_Edition 2.1_2022-09 (Amendment 1).pdf |  |  | KERI 20TC100154-R1_INSULATOR & PARTITION TEST.PDF |  | 32-TMSS-05-R1.pdf
1. International Standards/IEC | IEC 62271-110_Edition 4.0_2017-10.pdf |  |  | IEC 62271-110_Edition 4.0_2017-10.pdf |  |  | KERI 20TC100155-R1_연속개폐.pdf |  | 32-TMSS-05-R2.pdf
1. International Standards/IEC | IEC 62271-110_Edition 5.0_2023-03.pdf |  |  | IEC 62271-110_Edition 5.0_2023-03.pdf |  |  |  |  | 35-TMSS-01-R2.pdf
1. International Standards/IEC | IEC 62271-1_Edition 2.0_2017-07.pdf |  |  | IEC 62271-1_Edition 2.0_2017-07.pdf |  |  |  |  | 38-TMSS-07-R1.pdf
1. International Standards/IEC | IEC 62271-1_Edition 2.1_2021-10 (Amendment 1).pdf |  |  | IEC 62271-1_Edition 2.1_2021-10 (Amendment 1).pdf |  |  |  |  | TES-P-119.19-R1.pdf
1. International Standards/IEC | IEC 62271-203_Edition 2.0_2011-08.pdf |  |  | IEC 62271-203_Edition 2.0_2011-08.pdf
1. International Standards/IEC | IEC 62271-203_Edition 3.0_2022-05.pdf |  |  | IEC 62271-203_Edition 3.0_2022-05.pdf |  |  |  |  | Customer_Standard_Specifications__Spain__Iberdrola
1. International Standards/IEC | IEC 62271-204_Edition 1.0_2011-07.pdf |  |  | IEC 62271-204_Edition 1.0_2011-07.pdf |  |  |  |  | 00 CPC-AM GIS 132 kV.pdf
1. International Standards/IEC | IEC 62271-204_Edition 2.0_2022-05.pdf |  |  | IEC 62271-204_Edition 2.0_2022-05.pdf |  |  |  |  | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartA.pdf
1. International Standards/IEC | IEC 62271-209_Edition 2.0_2019-02.pdf |  |  | IEC 62271-209_Edition 2.0_2019-02.pdf |  |  |  |  | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartB.pdf
1. International Standards/IEC | IEC 62271-211_Edition 2.0_2024-09.pdf |  |  | IEC 62271-211_Edition 2.0_2024-09.pdf |  |  |  |  | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartC.pdf
1. International Standards/IEC | IEC 62271-306_Edition 1.0_2012-12.pdf |  |  | IEC 62271-306_Edition 1.0_2012-12.pdf |  |  |  |  | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartD.pdf
1. International Standards/IEC | IEC TR 62271-302_Edition 1.0_2010-06.pdf |  |  | IEC TR 62271-302_Edition 1.0_2010-06.pdf |  |  |  |  | 13 Desviaciones para i-DE respecto a INS 50.43.02_5.pdf
1. International Standards/IEC | IEC TR 62271-310_Edition 2.0_2008-03.pdf |  |  | IEC TR 62271-310_Edition 2.0_2008-03.pdf |  |  |  |  | INS 50.43.02_7-High Voltage Gas Insulated Switchgear for Substations.pdf
1. International Standards/IEC | IEC TS 62271-319_Edition 1.0_2024-09.pdf |  |  | IEC TS 62271-319_Edition 1.0_2024-09.pdf
1. International Standards/IEEE | IEEE Std C37.010-2016.pdf | [7 empty] | Customer_Standard_Specifications__Spain__REE
1. International Standards/IEEE | IEEE Std C37.04-2018.pdf | [7 empty] | ET082_ed8_Eng_NO_OFFICIAL.pdf
1. International Standards/IEEE | IEEE Std C37.04-2018_errata.pdf | [7 empty] | ET164_ed4_English_No_Official.pdf
1. International Standards/IEEE | IEEE Std C37.09-2018.pdf
1. International Standards/IEEE | IEEE Std C37.09-2018_errata.pdf
1. International Standards/IEEE | IEEE Std C37.122-2010.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KEMA 2515-15 V3(50-60Hz, 1.5).pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KEMA 2516-15 V3(50-60Hz, 1.3).pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KEMA 2517-15 V4(LC-CC, 50-60Hz 1.3-1.5).pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KEMA 2523-15 V3(60Hz, 1.5).pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KEMA 2524-15 V3(60Hz, 1.3).pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2016TC00558.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2016TC00736.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2016TC00925.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2017TC00055.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2017TC00070.pdf
2. Type Test Reports/145SP-3/145 kV 40 kA MS (2017) | KERI 2017TC00445.pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | CESI B9017250 TTR (60Hz).PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | CESI B9017251_TTR (50Hz).pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | CESI C0000059-1 TTC (60Hz).PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | CESI C0000060-1_TTC (50Hz).PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 19TB101031_LCCC.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100010_ES Induced current switching.pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100021_내아크.pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100025_OP2.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100027_Bus-transfer current switching tests.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100028-R1_ES Making.pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TB100029_STC.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100045_온도상승시험.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100065_LI AC PD RIV 보조회로 0기압.pdf
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100101_외함압력시험.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100102_IP TEST.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100154-R1_INSULATOR & PARTITION TEST.PDF
2. Type Test Reports/300SR/245 kV 50 kA MS (2020) | KERI 20TC100155-R1_연속개폐.pdf
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KEMA 3055-22 R0_Temperature rise.pdf
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KEMA 3078-22 R0_Mechanical_IP_Pressure.pdf
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 20TC100154_Insulator_Partition.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 22TB100134_Dielectric_RIV.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 22TB100169_STC.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 22TB100175_Internal.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 22TB100176_ES Making.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 23STL00038_Certificate.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 24TB100176_Out of phase switching.PDF
2. Type Test Reports/300SR/245 kV 63 kA MS (2024) | KERI 24TB100187_Capacitive switching.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | 111Sketch 1 - Typical 132kV GIS FDR process interface.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C General Specification - 132kV GIS - Jan 2022 Final.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C1 - ETS 0012 am0 - 66kV and 132kV pressurised GIS.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C2 - ETS0014 - Control panel fabrication and installation.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C3 - SDI 526 - Design of Substation Secondary Systems.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C4 - SDI 545 - Acceptable purity limits for SF6 gas.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C5 - SDI547 - Alarm and tripping requirements in SF6 and dry air equipment.pdf
3. Customer Standard Specifications/Australia/Endeavour Energy | Part C6 - SDI535 - Site testing and pre-commissioning.pdf
3. Customer Standard Specifications/Oman/OETC | 1. Standard Specification for Substation OETC-AMD-O-AMT-M-040.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 01-TMSS-01-R3.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 32-TMSS-02-R2-A1.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 32-TMSS-05-R1.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 32-TMSS-05-R2.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 35-TMSS-01-R2.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | 38-TMSS-07-R1.pdf
3. Customer Standard Specifications/Saudi Arabia/SEC | TES-P-119.19-R1.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 00 CPC-AM GIS 132 kV.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartA.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartB.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartC.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 12 INS 50-43-02_5_High voltage Gas-Insulated Switchgear for Substations-PartD.pdf
3. Customer Standard Specifications/Spain/Iberdrola | 13 Desviaciones para i-DE respecto a INS 50.43.02_5.pdf
3. Customer Standard Specifications/Spain/Iberdrola | INS 50.43.02_7-High Voltage Gas Insulated Switchgear for Substations.pdf
3. Customer Standard Specifications/Spain/REE | ET082_ed8_Eng_NO_OFFICIAL.pdf
3. Customer Standard Specifications/Spain/REE | ET164_ed4_English_No_Official.pdf